## Slide 1: FAULT DETECTION
Piero Baraldi,
Department of Energy, Politecnico di Milano

## Slide 2: Context: Prognostics and Health Management
Normal
operation
Remaining Useful Life
(RUL)
t
t
Detect
Diagnose
Predict
Equipment (System, Structure or Component)
c2
c1
c3
Measured
signals
Anomalous
operation
Malfunctioning type
(classes)
Notes: The object of PHM is in general a system or a component or a structure. Basically we will consider something that can degrade [digreid], deteriorate [diterioreit] and have a failure. And we will consider some measured signals which are somehow related with the operation and the health state of our system/structure or component. What we want to do is, first of all, to detect (ditect) if our system is in a normal opeartion condition or if there is a problem, anomalous/abnormal operatation. Inthis latter case we want to be able to diagnose the type of fault which has caused the anomaly. Finally we would also like to know the remaiing useful llife of our component that is the amount of time the equipment will continue to perform its function.

## Slide 3: In This Lecture: Fault Detection
Normal
operation
Remaining Useful Life
(RUL)
t
t
Detect
Diagnose
Predict
Equipment (System, Structure or Component)
c2
c1
c3
Measured
signals
Anomalous
operation
Malfunctioning type
(classes)
Notes: The object of PHM is in general a system or a component or a structure. Basically we will consider something that can degrade [digreid], deteriorate [diterioreit] and have a failure. And we will consider some measured signals which are somehow related with the operation and the health state of our system/structure or component. What we want to do is, first of all, to detect (ditect) if our system is in a normal opeartion condition or if there is a problem, anomalous/abnormal operatation. Inthis latter case we want to be able to diagnose the type of fault which has caused the anomaly. Finally we would also like to know the remaiing useful llife of our component that is the amount of time the equipment will continue to perform its function.

## Slide 4: Fault Detection: What is?
Measured
signals
Normal condition
Automatic algorithm
EQUIPMENT
Notes: Typically our equipment is in steady state, the signal that we monitor are …

## Slide 5: Fault Detection: What is?
Measured
signals
Normal condition
Automatic algorithm
EQUIPMENT

## Slide 6: Fault Detection: What is not?
Measured
signals
Normal condition
Automatic algorithm
EQUIPMENT
f1
f2

## Slide 7: Fault Detection: Approaches
Limit-based
Model-based
Data-driven

## Slide 8: Limit-based fault detection: data & information
Normal operation ranges of key signals
Normal operation
range
Abnormal condition
Abnormal condition
Pressurizer of a nuclear reactor
10.2 m
3.8 m
Water level
  Example:
time

## Slide 9: Limit-based fault detection: the method
Normal operation ranges of key signals
Limit Value-Based Fault Detection
Normal operation
range
Abnormal condition
Abnormal condition
Pressurizer of a nuclear reactor
10.2 m
3.8 m
  Example:
time
Water level

## Slide 10: Limit-based fault detection: Limitations
Normal operation ranges of key signals
Limit Value-Based Fault Detection
Normal operation
range
Abnormal condition
Abnormal condition
Pressurizer of a PWR nuclear reactor
10.2 m
3.8 m
  Example:
time
  Limitations:
  No early detection
  Not applicable to fault detection during operational transients
  Control systems operations may hide small anomalies (the signal remains in the normal range although there is a process anomaly)
  Considering signal individually can delay detection
Water level

## Slide 12: Fault Detection: Approaches
Limit-based
Model-based
Data-driven

## Slide 13: Model-based & Data-driven fault detection: basic idea
MODEL OF THE
EQUIPMENT BEHAVIOR
IN NORMAL CONDITION
Signal
reconstructions
Real
measurements
= ?
Statistical Test
Normal
Condition
Abnormal
Condition
Equipment

## Slide 14: Fault Detection: Approaches
Limit-based
Model-based
Data-driven

## Slide 15: Model-based fault detection: data & information
Physics-based model of the process (used to reproduce the expected behavior of the signals in normal condition)
Pressurizer model
Signal
reconstructions
  Example:

## Slide 16: Model-based fault detection: limitations
Abnormal Condition
  Typically not available for complex systems
  Long computational time
Pressurizer model
≠
Signal
reconstructions
Real
measurements
  Example:
Physics-based model of the process (used to reproduce the expected behavior of the signals in normal condition)

## Slide 17: Fault Detection: Approaches
Limit-Based
Model Based
Data-driven

## Slide 18: Data-driven fault detection: data & information
Historical signal measurements in normal operation
Water level
Pressure
Pressure | Liquid temperature | Steam temperature | Spray flow | Surge line flow | Heaters power | Level
150.2 | 321 | 362 | 539 | 244 | 0 | 7.2
150.4 | 322 | 363 | 681 | 304 | 0 | 7.5
150.3 | 323 | 364 | 690 | 335 | 1244 | 7.7
… | … | … | … | … | … | …
  Example:

## Slide 19: Example of Application 1*
19
COMPONENT TO Reactor Coolant Pump of PWR
BE MONITORED Nuclear Power Plant
x4
__________________________________________________
: 4
* Work developed with EDF-R&D
Measured signals | 48 (Temperatures, pressures, flows,…)
Available data | Historical signal measurements in normal plant condition [1 year, frequency=1/30 Hz]

## Slide 20: Example of Application 2
Measured signals | 6 vibration signals measured by accelerometers
Available data | Historical signal measurements in normal plant condition [3 years, frequency=5 kHz]
Notes: Generator, gearbox [giirbox], bearing

## Slide 21: Data-driven fault detection: possible methods
Statistical Approaches:
  AutoAssociative Kernel Regression (AAKR)
  Principal Component Analysis (PCA)-based
  …
Artificial Intelligence (AI)-based
  Feedforward Neural Networks (FNNs)
  AutoAssociative Neural Networks (AANNs)
  AutoEncoders (AEs)
  Self Organizing Maps
  …

## Slide 22: In This Lecture
MODEL OF THE
EQUIPMENT BEHAVIOR
IN NORMAL CONDITION
Signal
reconstructions
Real
measurements
Part 1
= ?
Statistical Test
Normal
Condition
Abnormal
Condition
Equipment
Part 2

## Slide 23: PART 1: Model of the Equipment Behaviour in Normal Condition
Auto Associative Kernel Regression (AAKR)
Principal Component Analysis (PCA)

## Slide 24: What do we need?
Data in normal conditions
obs-nc = observation in normal condition
Notes: Independently form the specific method…

## Slide 25: Training set, input and output
Model of the equipment behaviour in normal conditions
Signal
Observation
Training patterns: Historical signal measurements in normal condition
Test input: Signals measured at current time
Test Output: Signal reconstructions (expected values of the signals in normal condition)

## Slide 26: Requirement I
Equipment is in normal condition
t
t
Signal
Reconstructions
…
t
t
…
Real
Measurements
MODEL OF THE
EQUIPMENT BEHAVIOR
IN NORMAL CONDITION
reconstruction
nc= normal condition

## Slide 27: Requirement II
Equipment is in abnormal condition
t
t
Signal
Reconstructions
…
t
t
…
Real
Measurements
MODEL OF THE
EQUIPMENT BEHAVIOR
IN NORMAL CONDITION

## Slide 28: PART 1: Model of the Equipment Behaviour in Normal Condition
1A) Auto Associative Kernel Regression (AAKR)
1B) Principal Component Analysis (PCA)

## Slide 29: AAKR: Training set, input and output = Slide 21
AAKR
Signal
Observation
Training patterns: Historical signal measurements in normal condition
Test input: Signals measured at current time
Test Output: Signal reconstructions (expected values of the signals in normal condition)

## Slide 30: AAKR: the algorithm (1)
Training patterns:
Test input : measured signals at current time
Test output : weighted sum of the training patterns
x1
x2
On all the
training pattern
Notes: A weighted average of all observed j-th signal

## Slide 31: AAKR: the algorithm (2)
Output = weighted sum of the training patterns:
Notes: You associate a weight to each one of the training pattern.

## Slide 33: AAKR: the algorithm (2)
Output = weighted sum of the training patterns:
weights w(k) = similarity measures between and (the test and the k-th training pattern):
high weight
low weight
h = bandwidth parameter (it controls the decay speed)
Notes: You associate a weight to each one of the training pattern.

## Slide 34: AAKR: parameter h setting
d=0  w=0.40/h
d=h  w=0.24/h
d=2h  w=0.05/h
d=3h  w=0.004/h
w
d

## Slide 35: AAKR: the algorithm (2)
Output = weighted sum of the training patterns:
weights w(k) = similarity measures between and (the test and the k-th training pattern):
with Euclidean distance between and
high weight
low weight
Notes: You associate a weight to each one of the training pattern.

## Slide 36: AAKR: Exercise 1
Signal values at current time:
Historical signal measurements in normal plant condition:
x1
x2
Question 1) Where do you expect to be the
Signal reconstruction ?
Question 2) Is the plant in normal or abnormal conditions?

## Slide 37: Exercise 1: Solution
Signal values at current time:
Signal reconstructions: based on the available historical signal measurements in normal plant condition
x1
x2
normal condition

## Slide 38: AAKR: Exercise 2
Signal values at current time:
Historical signal measurements in normal plant condition:
Question 1) Where do you expect to be the
signal reconstruction ?
Question 2) Is the plant in normal or abnormal conditions?
x1
x2

## Slide 39: Exercise 2: Solution
x1
x2
available historical signal measurements in normal plant condition
abnormal condition
Signal values at current time:
Signal reconstructions: based on the available historical signal measurements in normal plant condition
Notes: The method is able to understand that in this case, of abnormal conditionm the relationship between x1 and x2 is different from the relationship between x1 and x2 in the training pattern, in the normal condition pattern.

## Slide 40: AAKR remarks: Computational Time
Computational time:
  No training of the model
  Test: computational time depends on a) the number of training patterns
  b) the number of signals
Notes: condition monitoring  on-line application. We want to know now if the plant is in a normal or abnormal condition. So, for example, if we have to wait 10 minutes for the computation of the output, the method would be not feaseable. In case of large

## Slide 41: AAKR remarks: Accuracy
Accuracy:
  depends on the training set:
    ↑N  ↑ Accuracy
x1
Few patterns and not well
distributed in the training space
Inaccurate reconstruction
x2
Notes: condition monitoring  on-line application. We want to know now if the plant is in a normal or abnormal condition. So, for example, if we have to wait 10 minutes for the computation of the output, the method would be not feaseable. In case of large

## Slide 42: AAKR remarks
Pros:
  No need of hypothesis on data distribution (e.g. linearity)
Cons
  Performance related to number of training observations

## Slide 43: PART 1: Model of the Equipment Behaviour in Normal Condition
1A) Auto Associative Kernel Regression (AAKR)
1B) Principal Component Analysis (PCA)

## Slide 44: PCA: What is it?
PCA:
  Space transformation
  From an n-dimensional space to a -dimensional space ()
  Retaining most of the information (loosing the least information)
x1
x2
x3
Notes: PCA is very famous and used techniques in many fields… Let us introduce it from a mathametical point of view. We have these points in a 3-dimensional space defined by x1,x2,x3 ….3 signals. A point can be described by giving its coordinate with respect to x1, x2 and x3 or by considering other 3 axes (changing reference system). PCA is first of all changing the reference system: it goes from x1,x2, xe to the one defined by PC1, PC2, and PC3…
In many applications we are interested to describe the information using less dimensions. In this case, for example, instead of using a reference system defined by n=3 axes, we want to use l=2 dimensions.
Now the questions is how to find the 2 dimensions with retaiing most of the information. We want to catch the intrinsic nature of the data by using only 2 dimensions. In this case for example the data form 3 clusters represented by … If we want to maintaining the clusters in 2 dimensions, a good representation is to consider the plane defined by PC1 and PC2 (reference system).

## Slide 45: IDEA OF PCA
Two signals are highly correlated or dependent One is enough!
Key underlying phenomena  Areas of variance in data  Focus on directions along which the observations have largest variance
Notes: Now, we have the problem of deciding which is the best reference system, the one that allows to loose the least information. Let us consider this trivial example … it is really needed to consider 2 dimensions to describe them? No this direction u is enough.
Now let us consider these other points that describe a physical phenomenon. What is meaningful from a physical point of view in these data? Probably, what is happening in the direction In red… What is the characteristic of this direction? It is the direction of maximum variability of the data. So, we can think that there is a process that is moving the data along the u direction, what is happening in the other directions can be thought as noise

## Slide 46: PCA: Training set, input and output = Slide 21 and Slide 25
PCA
Signal
Observation
Training patterns: Historical signal measurements in normal condition
Test input: Signals measured at current time
Test Output: Signal reconstructions (expected values of the signals in normal condition)
Notes: Now we go back to our problem of fault detection. We want to perform signal reconstructions. This is exactly the same problem setting that we have tackled with the AAKR

## Slide 47: PCA for fault detection: operational steps (1)
Step 1: find Principal Components (PCs) in the training set :
PC1 is the direction of maximum variance
PC2 is orthogonal to PC1 and describes the maximum residual variance
PC3 is orthogonal to PC1 and PC2 and describes the maximum residual variance

## Slide 48: Step 1: Mathematical details (1A)
Objective: find principal components
Procedure:
  Compute = covariance matrix of
Empirical
mean
matrix

## Slide 49: Step 1: Mathematical Details (1B)
Objective: find principal components
Procedure:
  Compute = covariance matrix of
  Find the n eigenvectors of and the corresponding eigenvalues
largest
smallest
=9.50
=0.04

## Slide 51: Step 1: Properties of the PCs (I)
  P is an orthonormal basis:

## Slide 52: Step 1: Properties of the PCs (II)
  P is an orthonormal basis:
  Data can be transformed from the original to the transformed bases and viceversa without any loss of information (multiplication for P and PT)
    = the projection of on the new basis is given by:

## Slide 53: Step 1: Properties of the PCs (III)
  P is an orthonormal basis:
  Data can be transformed from the original to the transformed bases and viceversa without any loss of information (multiplication for P and PT)
    = the projection of on the new basis is given by:
    can be obtained from by:

## Slide 54: Step 1: Properties of the PCs (III)
  P is an orthonormal basis:
  Data can be transformed from the original to the transformed bases and viceversa without any loss of information (multiplication for P and PT)
    = the projection of on the new basis is given by:
    can be obtained from by:
  The percentage of variance retained by the i-th principal component is:

## Slide 55: PCA for fault detection: operational steps (2)
Lost small information
Reduce the number of dimensions from n=10 to = 4
Step 2 [PCA approximation]: ignore the PCs of lower significance.

## Slide 56: PCA for fault detection: operational steps (2)
Step 2 [PCA approximation]: ignore the PCs of lower significance.
  map the observation in a subspace identified by the first l eigenvectors :
  with [
PC2
PC1
PC1
We consider only the directions that are most meaningful in normal condition (directions of maximum variance)
Example of application to the normal condition data:

## Slide 57: PCA for fault detection: operational steps (3)
PC1
[
Example of application to the normal condition data:
We loose the noise in the space of the measured signals
Step 2 [PCA approximation]: ignore the PCs of lower significance.
  map the observation in a subspace identified by the first eigenvectors :
  with [
  Step 3: [Antitrasformation]: signal reconstructions

## Slide 58: PCA for fault detection: Summary
          Find from
Historical data

## Slide 59: PCA for fault detection: Summary
          Find from
Historical data
Measured signals at present time:
    Trasform and project
    Antitrasform
 normal condition
 abnormal condition
Signal reconstructions
I’m looking at the measurements
considering only the directions that
are most meaningful in normal
condition (directions of maximum variance)
I loose only the irrelevant noise
The process is changed

## Slide 60: Exercise 1
Measured signals at present time:
Signal reconstructions?
Normal or abnormal condition?
available historical signal measurements in normal plant condition

## Slide 61: Exercise 1: Solution
Measured signals at present time:
Step 1: find principal components: ,
available historical signal measurements in normal plant condition

## Slide 62: Exercise 1: Solution
Measured signals at present time:
Step 1: find principal components ,
PC1

## Slide 63: Exercise 1: Solution
Measured signals at present time:
Step 1: find principal components ,
Step 2 (PCA approximation): keep only 1 PC of ,i.e.
PC1

## Slide 64: Exercise 1: Solution
Measured signals at present time:
Step 1: find principal components
Step 2 (PCA approximation): keep only 1 PC of ,i.e.
Step 3 (antitrasform):
normal condition

## Slide 65: Exercise 2
Measured signals at present time:
Signal reconstructions?
Normal or abnormal condition?
available historical signal measurements in normal plant condition

## Slide 66: Exercise 2: Solution
Measured signals at present time:
Step 1: find principal components
Step 2 (PCA approximation): keep only 1 PC of ,i.e.
PC1

## Slide 67: Exercise 2: Solution
Measured signals at present time:
Step 1: find principal components
Step 2 (PCA approximation): keep only 1 PC of ,i.e.
PC1

## Slide 68: Exercise 2: Solution
Measured signals at present time:
Step 1: find principal components
Step 2 (PCA approximation): keep only 1 PC of ,i.e.
Step 3 (antitrasform):
Abnormal condition

## Slide 69: PCA remarks: computational time
Computational time:
Training time = computational time necessary to find the Principal Components is proportional to the number of measured signals
Execution time: very short (only 2 matrix multiplications)  OK for online applications

## Slide 70: PCA remarks: complex structure
Performance:
Unsatisfactory for dataset characterized by highly non-linear relationships

## Slide 71: Part 2: Statistical Test
MODEL OF THE
EQUIPMENT BEHAVIOR
IN NORMAL CONDITION
Signal
reconstructions
Real
measurements
Part 1
= ?
Statistical Test
Normal
Condition
Abnormal
Condition
Equipment
Part 2

## Slide 72: In This Lecture
Part 1: Model of the Equipment Behavior in Normal Condition
  1A) Auto Associative Kernel Regression (AAKR)
  1B) Principal Component Analysis (PCA)
Part 2: Statistical Test
  2A) Thresholds-Based
  2B) Q-Statistics
  2C) Sequential Probability Ratio Test (SPRT)

## Slide 73: PART 2: Statistical Test
Thresholds-based
Q Statistics
Sequential Probability Ratio Test (SPRT)

## Slide 74: Abnormal condition detection: decision
Basics of the decision: residual analysis
Methods
  Thresholds-based approach
  Stochastic approaches:
    Q Statistics
    Sequential Probability Ratio Test (SPRT)
Abnormal condition
Normal condition

## Slide 75: PART 2 B: Statistical Test
Thresholds-based
Q Statistics
Sequential Probability Ratio Test (SPRT)

## Slide 76: Thresholds-based
t
r
Abnormal condition
detection

## Slide 77: Thresholds-Based: Remarks
Too large thresholds  high missing alarm rates (β)
t
r
Normal conditions
t
r
Abnormal conditions
Too small thresholds  high false alarm rates (α)
Easy to apply
Thresholds setting is difficult and error-prone

## Slide 78: PART 2 B: Statistical Test
Thresholds-based
Q-Statistics
Sequential Probability Ratio Test (SPRT)

## Slide 79: Stochastic approaches
Residual (r)= random variable described by a probability law
The probability law is different in case of normal/abnormal condition
~
~
Abnormal condition
Normal condition
EXAMPLE

## Slide 80: Q statistics
Assuming the signal reconstructions at time are: ,
then the Q-stat at time is:
=
The Q-statistics (squared prediction error) is a metric that accounts for the amount of variance that is not captured by the chosen - dimensional PCA model, which represents the “normal behaviour” of the signals.

## Slide 81: Q Statistics
Let
is approximately
Theorem ,see Appendix 1, J.E. Jackson and G.S. Mudholkar, Technometrics, 21(3), (1979), 341-349
c
Equipment in normal condition  =0.9
Notes: c is a random quantity and it is a pivotal quantity. Its distribution does not depend from parameters. So I perfectly known its distribution. It means I can compute its percentile. Here I am considering the 90° percentile. The prob… is . Frome

## Slide 82: Q Statistics
t
Abnormal condition
detection
=0.1
FALSE POSITIVE
 =0.9

## Slide 83: PART 2 B: Statistical Test
General Idea
Q Statistics
Sequential Probability Ratio Test (SPRT)

## Slide 84: SPRT
sequence of residuals at time , where
Binary hypothesis test:
  Null hypothesis (H0) ≡ Normal condition
  Alternative hypothesis (H1) ≡ Abnormal condition
Notes: Here we consider the signals, one by one.

## Slide 86: SPRT: the decision
Not enough
information

## Slide 87: SPRT Theorem
False alarm
Missing alarm
Notes: How to fix the thresholds A and B? There is a theorem that can help us, as often in statistics (-;, The theorem uses other two parameters alpha and beta that have a clear statistical interpretation…
Alpha can be linked to the probability of false alarmrms …D1= decision abnormal when …
Why we shouldn’t choose alpha and beta verysmall???
No free lunch…  big uncertainty zone

## Slide 88: SPRT for the positive mean test
Null hypothesis (H0) ≡ Normal condition
Alternative hypothesis (H1) ≡ Abnormal condition
Sequential
Formula!

## Slide 89: SPRT: Example
Not enough
information
2
1
3
0
Not enough
information
t
Notes: Fare esempio alla lavagna

## Slide 90: SPRT: parameters to be set
the residual variance in normal condition (σ2)
the expected offset amplitude (μ1)
the maximum acceptable false alarm rate (α)
the maximum acceptable missing alarm rate (β)

## Slide 91: Example
Time interval | Simulated Offset
[0-200] | No
[201-400] | Yes (amplitude = 0.11)
[401-600] | Yes (amplitude = 0.23)
[601-800] | Yes (amplitude = 0.34)
[801-1000] | Yes (amplitude = 0.46)
observed
Notes: We have a plant, several signals,…, one one signals we apply an anomaly of intensity increasing with time. Show…, here you see the observed value… and the reconstruction obrtained by the AAKR… notice that … Spiegare piano il caso studio

## Slide 92: Example: residuals
No offset
Maximum offset

## Slide 93: Example: SPRT
Parameter | Value
α | 0.01
Β | 0.01
μ0 | 0
μ1 | 0.46
σ2 | 0.12
No offset
Maximum offset
Notes: Fare esempio alla lavagna

## Slide 94: SPRT: performance
Time interval | Offset | Estimated ASN | Number of times in which a normal condition has been detected | Number of times in which an abnormal condition has been detected
[0-200] | No | 1.2 | 150 | 2
[201-400] | amplitude = 0.11 | 1.9 | 70 | 5
[401-600] | amplitude = 0.23 | 2.4 | 15 | 17
[601-800] | amplitude = 0.34 | 2.1 | 0 | 94
[801-1000] | amplitude = 0.46 | 1.2 | 2 | 142
Average Sample Number (ASN) needed to deliver a decision

## Slide 95
Case Study 1:
Monitoring Reactor Coolant Pumps

## Slide 96: Case Study (EdF)
96
COMPONENT TO Reactor Coolant Pumps of a PWR
BE MONITORED Nuclear Power Plant
x4
__________________________________________________
MEASURED 94 signals, 48 of which considered
SIGNALS as most important by EdF experts
__________________________________________________
RECONSTRUCTION Auto-Associative Kernel Regression
MODEL (AAKR)
historical measurements
test measurements
reconstruction

## Slide 97: Problem Statement (EdF): hundreds of signals  Grouping
97
COMPARISON
AUTO-ASSOCIATIVE
MODEL OF PLANT BEHAVIOR IN NORMAL CONDITION
MODEL 1
MODEL 2
MODEL m
MEASURED
SIGNALS
…
Notes: Coarse of dimensionality

## Slide 98: Challenge: Optimal Grouping
98
COMPARISON
MODEL 1
MODEL 2
HOW TO GROUP SIGNALS
?
MEASURED
SIGNALS
MODEL m
…

## Slide 99: Approaches to signal grouping
99
HOW TO SPLIT THE SIGNALS INTO SUBGROUPS?
A-PRIORI CRITERIA
(signals divided on the basis of…)
location in the power plant
correlation
physical homogeneity
others

## Slide 100: Results
best a-priori grouping: “correlation”
Criticality: how to group the signals which have a low degree of correlation with all the others?
100
WHITE: high correlation (0.7 1]
GREY: medium correlation (0.4 0.7]
BLACK: low correlation [0 0.4]
4
11
33
signals
signals
signal belonging to group 1
signal belonging to group 2
signal belonging to group 3
signal belonging to group 4
signal belonging to group 5

## Slide 101: Results: reconstruction of simulated sensor failures
SENSOR: Temperature of the water flowing to the first seal of the pump in line 1:
Failure 2 = sensor offset
Failure 3 =sensor stuck
Failure 1 = measurement noise increase
residual
residual
residual
Fault injection
Notes: To test the method before its use, we have simulated data over normal conditions. In practice …

## Slide 102: Results: seal deterioration detection
102
COMPARISON
DECISION
ŝ1
t
t
s1 – ŝ1
t
s1
ABNORMAL CONDITION: seal deterioration
(seal
outcoming
flow)
MEASURED SIGNALS
NORMAL
CONDITION
ABNORMAL
CONDITION
AUTO-ASSOCIATIVE MODEL OF PLANT BEHAVIOR IN NORMAL CONDITIONS

## Slide 103: Data-Driven Fault Detection
Challenges?

## Slide 104: Data-Driven Fault Detection: Challenge I
Hundreds of signals are monitored
EMPIRICAL MODEL OF
PLANT BEHAVIOR
IN NORMAL OPERATION
(AAKR, PCA, ANN)
Signal
reconstructions
DIFFICULT TO DEVELOP

## Slide 105: Fault Detection: Challenge I
Measured
Signals
Group generation
Subset 2
Subset 1
Subset H
Model 2
Model 1
Model H
Random
Solution
123 signals
≈30 signals
…
Ensemble of models

## Slide 106: Fault Detection: Challenge I
Measured
Signals
Group generation
Subset 2
Subset 1
Subset H
Model 2
Model 1
Model H
Random
Solution
123 signals
≈20 signals
…
Aggregation
Weighted
Average
Ensemble of models

## Slide 107: Fault Detection: Challenge II
Evolving Environment
Inlet Gas
Temperature
2012
2015
2019
Plammed Maintenance
Operational Condition:
Load 100% 
Load 80%
Plant Upgrading: Valve ‘64y’ is replaced with a new model

## Slide 108: Fault Detection: Challenge II
t0
T
P
Identify historical signal measurements in
normal plant operation
T
P
time
False
alarm
rate
t0
t1
A New Model is necessary
Plant operations slowly
change with time
Develop the model
Example: monitoring the turbine of an electric power plant

## Slide 109: Fault Detection: Challenge II
time
False
alarm
rate
t0
t1
A New Model is necessary
t1
T
time
False
alarm
rates
t0
t1
T
P
Identify recent historical signal measurements in
normal plant operation
Develop the new model
Periodic Human Interventions for developing new models!  high costs!
P
Example: monitoring the turbine of an electric power plant
t0
T
P
Identify historical signal measurements in
normal plant operation
T
P
Develop the model
Plant operations slowly
change with time

## Slide 110: Fault Detection: Challenge II
The detection model should be able to follow the process changes:
Incremental learning of the new data that gradually becomes available
No necessity of human intervention for:
  selecting recent normal operation data
  building the new model
T
P
T
P
New data are coming
T
P
Automatic updating of the model

## Slide 111: Fault Detection: Challenge III
Robustness of the Reconstruction
ROBUSTNESS:
t
t
t
t
ABNORMAL CONDITION
M
O
D
E
L
OK
Signal
reconstructions
Real
measurements

## Slide 112: Example: Monitoring a Turbine for Energy Production
6 Temperature Sensors
in different position
 | 1 | 0.97 | 0.98 | 0.98 | 0.99 | 0.98
 | 0.97 | 1 | 0.95 | 0.99 | 0.98 | 0.96
 | 0.98 | 0.95 | 1 | 0.96 | 0.99 | 0.99
 | 0.98 | 0.99 | 0.96 | 1 | 0.98 | 0.97
 | 0.99 | 0.98 | 0.99 | 0.98 | 1 | 0.99
 | 0.98 | 0.96 | 0.99 | 0.97 | 0.99 | 1
 | 1 | 0.97 | 0.98 | 0.98 | 0.99 | 0.98
 | 0.97 | 1 | 0.95 | 0.99 | 0.98 | 0.96
 | 0.98 | 0.95 | 1 | 0.96 | 0.99 | 0.99
 | 0.98 | 0.99 | 0.96 | 1 | 0.98 | 0.97
 | 0.99 | 0.98 | 0.99 | 0.98 | 1 | 0.99
 | 0.98 | 0.96 | 0.99 | 0.97 | 0.99 | 1
Highly Correlated Signals
Abnormal condition of the first signal

## Slide 113: Example: Traditional AAKR
1
2
Simulated abnormal conditions
Simulated abnormal conditions
DELAY IN THE DETECTION
IMPOSSIBILITY TO IDENTIFY THE SIGNALS
TRIGGERING THE ABNORMAL BEHAVIOR
Notes: Spill-over…

## Slide 114: Our Contribution: A modified AAKR method
Modified AAKR
-
Fault
Detection
No Fault
Fault
Modification of the loci
of equisimilarity points
Malfunctions causing variations
of a small number of signals are
more frequent than those
causing variations of a large
number of signals

## Slide 115: Results
Early Detection
More Accurate
Correct Diagnosis of the signal that triggers the alarms

## Slide 116: Modified AAKR
 | Traditional AAKR | Modify AAKR
Loci of equisimilarity points |  | 
Accuracy | OK! | OK!
Robustness | NO! Especially with correlated signals | Robust reconstruction of the values expected in normal conditions Correct identification of signals affected by abnormal condition Good performance with correlated signals

## Slide 117: Fault Detection - Challenges
Hundreds of Signals are Monitored
Evolving Environment
Robustness
…